# WESTERN KENTUCKY UNIVERSITY

DEPARTMENT OF ENVIRONMENTAL HEALTH AND SAFETY

FACILITIES DESIGN & CONSTRUCTION STANDARDS

SECTION KBC 906

NATIONAL FIRE PROTECTION ASSOCIATION

FIRE EXTINGUISHERS AND CABINETS

# PART 1 GENERAL

1.1 SUMMARY

A.    Section includes fire extinguishers; fire extinguisher cabinets; and brackets for wall mounting.

B.    This standard is provided to obtain and maintain adequate, approved fire protection equipment for Western    Kentucky University Campus.  Any questions regarding this standard shall be directed to Western Kentucky

University, EHS Fire Safety Officer.    (270/745-2931)

C.   In general, all fire protection design issues are subject to internal review and approval by the Department of

EH&S Fire Safety Officer.

1.2 Kentucky Building Code REFERENCES

A. Fire Extinguishers Study Guide, as published by the Office of State Fire Marshal.

B. UL (Underwriters Laboratories, Inc.) - Fire Protection Equipment Directory

KBC chapter 9 section 906 and NFPA 10

D. Kentucky Fire Code

1.3 SUBMITTALS

A       Architectural Drawings: Indicate cabinet physical dimensions, rough-in measurements for recessed cabinets, wall bracket mounted measurements, location, fire ratings, and manufacturer’s data sheets for extinguisher cabinets and other accessories. The location and type of all fire extinguishers shall be identified in a schedule format on the architectural drawings.

B.     The Project Manager will submit the drawings to the University Fire Marshal’s Office for internal review. After receiving comments, the contractor shall make appropriate changes to the drawings. For any requirements not implemented, design consultant/contractor shall provide an explanation in writing.

C.     Drawings shall be compatible with WKU-FO/Maps and Records department standards, and shall include:

1. Floor plans showing location and type of all fire extinguishers, cabinets and signs.

2. Elevations showing mounting heights for extinguishers, cabinets and signs.

3. Details of sign graphics and language.

D. Manufacturer’s data sheets for all types of fire extinguisher cabinets, signs and other accessories shall be submitted. Exact model shall be indicated on the data sheet when more than one model is shown.

1. Include physical dimensions, operational features, color and finish, anchorage details, rough-in measurements, location and details.

E. Record Drawings and Maintenance Data: At completion of the work and prior to final inspection, the Contractor shall turn over to the Project Manager two sets of a record drawing showing the location of each extinguisher and other installed hardware. Record drawing shall be a maximum size of 11’x17’.

1.4 QUALITY ASSURANCE

A. Conform to and comply with NFPA 10 Reference A-1-1, requirements for extinguisher installation and identification.

B. Competency Quotation: The work shall be performed by a Contractor who shall have had at least 5 years successful installing cabinets, brackets signs and other accessories of similar make and similar model. The Project Manager may reject any proposed installer who cannot show evidence of such qualifications.

ENVIRONMENTAL REQUIREMENTS

A. Interior cabinets shall only be located in interior locations. Exterior locations shall utilize weather-proof cabinets.

# PART 2 PRODUCTS

- 2.1

FIRE EXTINGUISHERS – The Project Manager is responsible to submit a Service Request Form for all fire extinguisher units required to WKU / FMO. Fire protection cabinets are to be furnished and installed by the Contractor. The fire extinguishers are furnished, tagged and installed by WKU/FMO.

- Minimum Type and Location:

- 4A-60BC extinguishers in all common areas, elevator control rooms, generators and the building     mechanical rooms.

- 5# CO2-BC extinguishers in all chemical labs. 10-BC extinguishers in all mechanical and electrical rooms.

- Carbon Dioxide Fire Extinguishers are be located in all commercial kitchens.

- All commercial Kitchens shall be equipped with Rangehood suppression systems.

- Computer Rooms – type as required by State Fire Marshal office and WKU/FMO.

B. Halon: Not permitted for new installations.  FM/ 200 or CO2 Systems are acceptable units.

C. Water Type:   Use for Class A type environments only.

D.  Special Hazard Conditions: Refer to WKU/FMO to determine the appropriate type of extinguisher.

  - The minimum number of extinguishers and spacing shall be as required by KBC and NFPA 10 Reference A-1-1. The preferred location for extinguishers is adjacent to exits.

2.2 FIRE EXTINGUISHER CABINETS

A. Configuration:  Semi recessed or recessed cabinets are preferred.

Exception: Exterior weather-proof cabinets may be surface mounted.

B. Door: Latch access only, key lock access is not acceptable. Cabinet doors shall be equipped with a vision panel.

C. Door Glazing: Break glass type cabinets are not acceptable.

D. Cabinet interiors to have a minimum clear space of 18 inches high by 8 inches wide and capable of containing the specified fire extinguisher.

E.  Cabinet Finish: Project Architect shall specify finish type available from the manufacturer.

# PART 3 EXECUTION

3.1 EXTINGUISHER INSTALLATION

A. Contractor shall install fire extinguisher cabinets following all manufactures specifications.

3.2 CABINET INSTALLATION

A. Prepare structural members of backing as required for mounting screws.

B. Installation of cabinets using nails is not acceptable.

C. Ensure cabinets are secured rigidly in place in accordance with manufacturer’s instructions. Minimum of two screws each at both the top and bottom of the rear of the cabinet anchored to building structural members or backing attached to structural members. Verify that the cabinet mounting holes line up with structural members or backing.

D. Install fire extinguishers in cabinets at the completion of construction. Cabinets shall be

located so that the hinge door has a clear opening dimension of 180 degrees.

E. Fire extinguisher cabinets shall be installed so that the bottom of the cabinet is not more than 2 ft. above the        floor.

- 3.3   BRACKET INSTALLATION – Contact WKU/FMO at 745-2931 to coordinate installation.

- A.  Brackets for hanging fire extinguishers will normally be installed by WKU/FMO.

- B.  Alternate installation methods shall be reviewed and approved by WKU/FMO.

3.4 WARRANTY

A. Contractor shall warranty cabinets, accessories, and workmanship for a period of one (1) year from the date of final acceptance.

END OF SECTION